{"text_format":"2","workbook":"xlsx","n_sheets":4,"sheets":["固液分离处理单元","沼液浓缩单元1","沼液浓缩单元2","方案相关表格"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"固液分离处理单元","index":0,"n_rows":34,"n_cols":16,"rows_kept":34,"cut":false,"hidden":false,"merged":[[17,5,24,5]]}
["名称","对应字段(K)","布尔量说明(V)","写权限(0:只读|1:读写）","对应流程图中组件","备注"]
["EM0_输出0","EM0_out0",null,0,"查看下面的工艺流程图","此变量不做"]
["EM0_输出1","EM0_out1",null,0,null,"此变量不做"]
["EM0_输出2","EM0_out2",null,0,null,"此变量不做"]
["EM0_输出3","EM0_out4",null,0,null,"此变量不做"]
["原料泵过载","ylbgz_zt","0:正常|1:故障",0]
["挤出机过载","jcjgz_zt","0:正常|1:故障",0]
["振动电机过载","zddjgz_zt","0:正常|1:故障",0]
["振荡筛过载","zdsgz_zt","0:正常|1:故障",0]
["上料泵过载","slbgz_zt","0:正常|1:故障",0]
["排污泵过载","pwbgz_zt","0:正常|1:故障",0,{"$nulls":8},"控制项","操作字段","有效值","反馈字段"]
["原料池高液位","ylcgyw_zt","0:正常|1:高液位",0,{"$nulls":8},"原料泵输出","ylbsc_sz","0:关闭|1:打开","ylbsc_sz"]
["原料池低液位","ylcdyw_zt","0:正常|1:低液位",0,{"$nulls":8},"挤出机输出","jcbsc_sz","0:关闭|1:打开","jcbsc_sz"]
["污水池高液位","wscgyw_zt","0:正常|1:高液位",0,{"$nulls":8},"振动电机输出","zddjsc_sz","0:关闭|1:打开","zddjsc_sz"]
["污水池低液位","wscdyw_zt","0:正常|1:低液位",0,{"$nulls":8},"振荡筛输出","zdssc_sz","0:关闭|1:打开","zdssc_sz"]
["滤液池高液位","lycgyw_zt","0:正常|1:高液位",0,{"$nulls":8},"上料泵输出","slbsc_sz","0:关闭|1:打开","slbsc_sz"]
["滤液池低液位","lycdyw_zt","0:正常|1:低液位",0,{"$nulls":8},"排污泵输出","pwbsc_sz","0:关闭|1:打开","pwbsc_sz"]
["原料泵输出","ylbsc_sz","0:关闭|1:打开",1,null,"组件级控制",{"$nulls":6},"滤液泵输出","lybsc_sz","0:关闭|1:打开","lybsc_sz"]
["挤出机输出","jcbsc_sz","0:关闭|1:打开",1,{"$nulls":8},"原料泵输出","bjsc_sz","0:关闭|1:打开"]
["振动点击输出","zddjsc_sz","0:关闭|1:打开",1]
["振荡筛输出","zdssc_sz","0:关闭|1:打开",1]
["上料泵输出","slbsc_sz","0:关闭|1:打开",1]
["排污泵输出","pwbsc_sz","0:关闭|1:打开",1]
["滤液泵输出","lybsc_sz","0:关闭|1:打开",1]
["报警输出","bjsc_sz","0:关闭|1:打开",1]
["自动运行开/关","zdmskg_sz","0:关闭|1:打开",1,null,"系统级控制"]
[]
[]
[null,"故障状态，该状态支持故障预警及远程设置"]
[null,"组件状态，该状态支持故障预警及远程设置"]
[null,"系统级远程控制，支持远程远程设置"]
[null,"组件级远程控制，支持远程远程设置"]
[]
["系统级远程控制为自动模式开关。该模式打开后，组件级的控制由现场PLC控制器自行控制。该模式关闭后，才可以使用组件级远程控制。"]

{"sheet":"沼液浓缩单元1","index":1,"n_rows":87,"n_cols":11,"rows_kept":87,"cut":false,"hidden":false,"merged":[[83,5,86,5],[42,4,43,4]]}
["名称","对应字段(K)","布尔量说明(V)","写权限(0:只读|1:读写）","对应流程图中组件","备注"]
["过滤水箱低液位开关状态","glsxdyw_zt","0:正常|1:低液位",0,"沼液箱液位"]
["过滤水箱高液位开关状态","glvsgyw_zt","0:正常|1:高液位",0]
["中间水箱1低液位开关状态","zjsx1dyw_zt","0:正常|1:低液位",0,"中间水箱1液位"]
["中间水箱1高液位开关状态","zjsx1gyw_zt","0:正常|1:高液位",0]
["进水阀1开反馈状态","jsf1kfk_zt","0:不确定状态|1:打开成功",0,"UF增压泵1后的进水阀"]
["进水阀1关反馈状态","jsf1gfk_zt","0:不确定状态|1:关闭成功",0]
["冲洗阀1开反馈","cxf1kfk_zt","0:不确定状态|1:打开成功",0,"UF增压泵1后的冲洗阀"]
["冲洗阀1关反馈","cxf1gfk_zt","0:不确定状态|1:关闭成功",0]
["循环阀1开反馈","xhf1kfk_zt","0:不确定状态|1:打开成功",0,"UF1循环阀"]
["循环阀1关反馈状态","xhf1gfk_zt","0:不确定状态|1:关闭成功",0]
["上排阀1开反馈状态","spf1kfk_zt","0:不确定状态|1:打开成功",0,"UF1上排阀"]
["上排阀1关反馈状态","spf1gfk_zt","0:不确定状态|1:关闭成功",0]
["下排阀1开反馈状态","xpf1kfk_zt","0:不确定状态|1:打开成功",0,"UF1下排阀"]
["下排阀1关反馈状态","xpf1gfk_zt","0:不确定状态|1:关闭成功",0]
["反洗阀1开反馈","fxf1kfk_zt","0:不确定状态|1:打开成功",0,"UF1反洗阀"]
["反洗阀1关反馈","fxf1gfk_zt","0:不确定状态|1:关闭成功",0]
["产水阀1开反馈状态","csf1kfk_state","0:不确定状态|1:打开成功",0,"UF1产水阀"]
["产水阀1关反馈","csf1gfk_zt","0:不确定状态|1:关闭成功",0]
["产排阀1开反馈状态","cpf1kfk_zt","0:不确定状态|1:打开成功",0,"UF1产水排放阀"]
["产排阀1关反馈状态","cpf1gfk_zt","0:不确定状态|1:关闭成功",0]
["NF进水压力状态","NFjsyl_zt","0:正常|1:NF高压泵进水压力过低",0,"NF高压泵前压力过低"]
["NF产水高压","NFcsgy_zt","0:正常|1:NF高压泵产水压力过高",0,"NF高压泵后压力过高"]
["NF冲洗阀开反馈状态","NFcxfkfk_zt","0:不确定状态|1:打开成功",0,"NF冲洗阀"]
["NF冲洗阀关反馈状态","NFcxfgfk_zt","0:不确定状态|1:关闭成功",0]
["NF高压泵运行状态","NFgybyx_zt","0:正常|1:NF高压泵运行",0,"NF高压泵"]
["NF高压泵故障状态","NFgybgz_zt","0:正常|1:NF高压泵故障",0]
["膜冲洗泵1运行状态","mcxb1yx_zt","0:正常|1:膜冲洗泵运行",0,"UF冲洗泵"]
["膜冲洗泵1故障状态","mcxb1gz_zt","0:正常|1:膜冲洗泵故障",0]
["增压泵1运行状态","zyb1yx_zt","0:正常|1:增压泵1运行",0,"UF增压泵"]
["增压泵1故障状态","zyb1gz_zt","0:正常|1:增压泵1故障",0]
["阻垢剂加药计量泵1运行状态","zgjjlb1yx_zt","0:正常|1:阻垢剂计量泵运行",0,"阻垢剂泵"]
["PH加药计量泵运行状态","PHjlbyx_zt","0:正常|1:PH加药计量泵运行",0,"PH加药泵"]
["抑菌剂加药计量泵运行状态","yjjjlbyx_zt","0:正常|1:抑菌剂计量泵运行",0,"抑菌剂泵"]
["运行时间设定-UF1系统","UF1yxsj_sz",null,1]
["上反洗时间设定-UF1系统","UF1sfxsj_sz",null,1]
["下反洗时间设定-UF1系统","UF1xfssj_sz",null,1]
["正洗时间设定-UF1系统","UF1zxsj_sz",null,1]
["运行剩余时间显示-UF1系统","UF1yxsysj_xs",null,0]
["上反洗剩余时间显示-UF1系统","UF1sfxsysj_xs",null,0,null,null,null,"参数项","操作字段"]
["下反洗剩余时间显示-UF1系统","UF1xfssysj_xs",null,0,null,null,null,"UF1运行时间","UF1yxsj_sz"]
["正洗剩余时间显示-UF1系统","UF1zxsysj_xs",null,0,null,null,null,"UF1上反洗时间","UF1sfxsj_sz"]
["启动-点动-UF1系统","UF1qd_sz","0:无意义|1:启动",1,"与随后的“待机”“运行“状态对应。远程开机：启动=1，停机=0，开机成功，则停机=0，运行=1；远程停机：启动=0，停机=1，停机成功则停机=1，运行=0",null,null,"UF1下反洗时间","UF1xfssj_sz"]
["停机-点动-UF1系统","UF1tj_sz","0:无意义|1:停机",1,null,null,null,"UF1正洗时间","UF1zxsj_sz"]
["待机-UF1系统","UF1dj_sz","0:正常|1:待机",0,null,null,null,"NF高压泵频率","NFgybpl_sz"]
["运行-UF1系统","UF1yx_sz","0:正常|1:运行",0,null,null,null,"膜冲洗泵1频率","mcxb1pl_sz"]
["上反洗-UF1系统","UF1sfx_sz","0:正常|1:上反洗",0,null,null,null,"UF增压泵1频率号","UFzyb1pl_sz"]
["下反洗-UF1系统","UF1xfx_sz","0:正常|1:下反洗",0,null,null,null,"NF开机冲洗时间","NFkjcxsj_sz"]
["正洗-UF1系统","UF1zx_sz","0:正常|1:正洗",0,null,null,null,"NF运行时间","NFyxsj_sz"]
["反洗-UF1系统","UF1fx_sz","0:正常|1:反洗",0,null,null,null,"NF停机冲洗时间","NFtjcxsj_sz"]
["NF高压泵频率给定信号","NFgybpl_sz",null,0]
["膜冲洗泵1频率给定信号","mcxb1pl_sz",null,0]
["UF增压泵1频率给定信号","UFzyb1pl_sz",null,0]
["NF开机冲洗时间设定-NF系统","NFkjcxsj_sz",null,1]
["NF运行时间设定-NF系统","NFyxsj_sz",null,1]
["NF停机冲洗时间设定-NF系统","NFtjcxsj_sz",null,1]
["NF开机冲洗剩余时间显示-NF系统","NFkjcxsysj_xs",null,0]
["NF运行剩余时间显示-NF系统","NFyxsysj_xs",null,0,null,null,null,"控制项","操作字段","有效值","反馈字段"]
["NF停机冲洗剩余时间显示-NF系统","NFtjcxsjxs_xs",null,0,null,null,null,"UF1启动","UF1qd_sz","0:无意义|1:启动","UF1yx_sz"]
["启动-NF系统","NFqd_sz","0:无意义|1:启动",1,"同UF1启动停机功能",null,null,"UF1停机","UF1tj_sz","0:无意义|1:停机","UF1dj_sz"]
["停机-NF系统","NFtj_sz","0:无意义|1:停机",1,null,null,null,"NF启动","NFqd_sz","0:无意义|1:启动","NFyx_sz"]
["急停-NF系统","NFjt_sz","0:正常|1:急停",1,null,null,null,"NF停机","NFtj_sz","0:无意义|1:停机","NFdj_sz"]
["待机-NF系统","NFdj_sz","0:正常|1:待机",0,null,null,null,"UF2启动","UF2qd_sz","0:无意义|1:启动","slbsc_sz"]
["开机冲洗-NF系统","NFkjcx_sz","0:正常|1:开机冲洗",0,null,null,null,"UF2停机","UF2tj_sz","0:无意义|1:停机","pwbsc_sz"]
["运行-NF系统","NFyx_sz","0:正常|1:运行",0,null,null,null,"RO启动","lybsc_sz","0:无意义|1:启动","lybsc_sz"]
["停机冲洗-NF系统","NFtjcx_sz","0:正常|1:停机冲洗",0,null,null,null,"RO停机","bjsc_sz","0:无意义|1:停机"]
[]
["系统1启动","xt1qd_sz","0:无意义|1:启动",1]
["系统1停止","xt1tz_sz","0:无意义|1:停止"]
[]
[null,"故障状态。该状态支持故障预警及远程设置"]
[null,"组件状态，该状态支持故障预警及远程设置"]
[null,"组件状态。该状态仅展示即可"]
[null,"流程状态。只做展示"]
[null,"系统参数。展示及可远程设置"]
[null,"系统级远程控制，支持远程远程设置"]
[null,"二级系统级控制。展示及可远程设置"]
[null,"暂时不做"]
[]
[]
[]
[{"$nulls":5},"设备","控制项","控制项","控制项","控制项"]
[{"$nulls":5},"固液分离单元","自动运行开关","zdmskg_sz","1：启动|0：停止","zdmskg_sz"]
[{"$nulls":5},"沼液浓缩单元","系统1启动","xt1qd_sz","1：启动|0：无意义","xt1qd_sz"]
[{"$nulls":6},"系统2启动","Xt2qd_sz","1：启动|0：无意义","Xt2qd_sz"]
[{"$nulls":6},"系统1停止","xt1tz_sz","1：停止 |0：无意义","xt1tz_sz"]
[{"$nulls":6},"系统2停止","Xt2tz_sz","1：停止 |0：无意义","Xt2tz_sz"]

{"sheet":"沼液浓缩单元2","index":2,"n_rows":103,"n_cols":11,"rows_kept":103,"cut":false,"hidden":false,"merged":[[45,4,46,4]]}
["名称","对应字段(K)","布尔量说明(V)","写权限(0:只读|1:读写）","对应流程图中组件","备注"]
["中间水箱2低液位开关","zjsx2dyw_zt","0:正常|1:故障",0,"中间水箱"]
["中间水箱2高液位开关","zjsx2gyw_zt","0:正常|1:故障",0]
["冲洗水箱低液位开关","cxsxdyw_zt","0:正常|1:故障",0,"冲洗水箱"]
["冲洗水箱高液位开关","cxsxgyw_zt","0:正常|1:故障",0]
["进水阀2开反馈","jsf2kfk_zt","0:正常|1:故障",0,"UF增压泵1后的进水阀"]
["进水阀2关反馈","jsf2gfk_zt","0:正常|1:故障",0]
["冲洗阀2开反馈","cxf2kfk_zt","0:正常|1:故障",0,"UF增压泵1后的冲洗阀"]
["冲洗阀2关反馈","cxf2gfk_zt","0:正常|1:故障",0]
["循环阀2开反馈","xhf2kfk_zt","0:正常|1:故障",0,"UF1循环阀"]
["循环阀2关反馈","xhf2gfk_zt","0:正常|1:故障",0]
["上排阀2开反馈","spf2kfk_zt","0:正常|1:故障",0,"UF1上排阀"]
["上排阀2关反馈","spf2gfk_zt","0:正常|1:故障",0]
["下排阀2开反馈","xpf2kfk_zt","0:正常|1:故障",0,"UF1下排阀"]
["下排阀2关反馈","xpf2gfk_zt","0:正常|1:故障",0]
["反洗阀2开反馈","fxf2kfk_zt","0:正常|1:故障",0,"UF1反洗阀"]
["反洗阀2关反馈","fxf2gfk_zt","0:正常|1:故障",0]
["产水阀2开反馈","csf2kfk_zt","0:正常|1:故障",0,"UF1产水阀"]
["产水阀2关反馈","csf2gfk_zt","0:正常|1:故障",0]
["产排阀2开反馈","cpf2kfk_zt","0:正常|1:故障",0,"UF1产水排放阀"]
["产排阀2关反馈","cpf2gfk_zt","0:正常|1:故障",0]
["RO进水压力","ROjsyl_zt","0:正常|1:故障",0,"RO高压泵前压力过低"]
["RO产水高压","ROcsgy_zt","0:正常|1:故障",0,"RO高压泵后压力过高"]
["RO冲洗阀开反馈","ROcxfkfk_zt","0:正常|1:故障",0,"RO冲洗阀"]
["RO冲洗阀关反馈","ROcxfgfk_zt","0:正常|1:故障",0]
["RO高压泵运行","ROgybyx_zt","0:正常|1:故障",0,"RO高压泵"]
["RO高压泵故障","ROgybgz_zt","0:正常|1:故障",0]
["UF增压泵2运行","UFzyb2yx_zt","0:正常|1:故障",0,"UF2增压泵"]
["UF增压泵2故障","UFzyb2gz_zt","0:正常|1:故障",0]
["膜冲洗泵2运行","mcxb2yx_zt","0:正常|1:故障",0,"冲洗水箱后边的冲洗泵"]
["膜冲洗泵2故障","mcxb2gz_zt","0:正常|1:故障",0]
["NF增压泵运行","NFzybyx_zt","0:正常|1:故障",0,"NF增压泵"]
["NF增压泵故障","NFzybgz_zt","0:正常|1:故障",0]
["RO增压泵运行","ROzybyx_zt","0:正常|1:故障",0,"RO增压泵"]
["RO增压泵故障","ROzybgz_zt","0:正常|1:故障",0]
["生物减灭器运行","swjmqyx_zt","0:正常|1:故障",0]
["阻垢剂加药计量泵2运行","zgjjlb2yx_zt","0:正常|1:故障",0,"阻垢剂加药装置2"]
["运行时间设定-UF2系统","UF2yxsj_sz",null,1]
["上反洗时间设定-UF2系统","UF2sfxsj_sz",null,1]
["下反洗时间设定-UF2系统","UF2xfssj_sz",null,1]
["正洗时间设定-UF2系统","UF2zxsj_sz",null,1]
["运行剩余时间显示-UF2系统","UF2yxsysj_xs",null,0]
["上反洗剩余时间显示-UF2系统","UF2sfxsysj_xs",null,0,null,null,null,"控制项","操作字段","有效值","反馈字段"]
["下反洗剩余时间显示-UF2系统","UF2xfssysj_xs",null,0,null,null,null,"UF1启动","UF1qd_sz","0:无意义|1:启动","UF1yx_sz"]
["正洗剩余时间显示-UF2系统","UF2zxsysj_xs",null,0,null,null,null,"UF1停机","UF1tj_sz","0:无意义|1:待机","UF1dj_sz"]
["启动-点动-UF2系统","UF2qd_sz","0:无意义|1:启动",1,"与随后的“待机”“运行“状态对应。远程开机：启动=1，停机=0，开机成功，则停机=0，运行=1；远程停机：启动=0，停机=1，停机成功则停机=1，运行=0",null,null,"NF启动","NFqd_sz","0:无意义|1:启动","NFyx_sz"]
["停机-点动-UF2系统","UF2tj_sz","0:无意义|1:停机",1,null,null,null,"NF停机","NFtj_sz","0:无意义|1:待机","NFdj_sz"]
["待机-UF2系统","UF2dj_sz","0:正常|1:待机",0,null,null,null,"UF2启动","UF2qd_sz","0:无意义|1:启动","UF2yx_sz"]
["运行-UF2系统","UF2yx_sz","0:正常|1:运行",0,null,null,null,"UF2停机","UF2tj_sz","0:无意义|1:待机","UF2dj_sz"]
["上反洗-UF2系统","UF2sfx_sz","0:正常|1:上反洗",0,null,null,null,"RO启动","ROqd_sz","0:无意义|1:启动","ROyx_sz"]
["下反洗-UF2系统","UF2xfx_sz","0:正常|1:下反洗",0,null,null,null,"RO停机","ROtj_sz","0:无意义|1:待机","ROdj_sz"]
["正洗-UF2系统","UF2zx_sz","0:正常|1:正洗",0]
["反洗-UF2系统","UF2fx_sz","0:正常|1:反洗",0]
["RO开机冲洗时间设定-NF系统","ROkjcxsj_sz",null,1]
["RO运行时间设定-NF系统","ROyxsj_sz",null,1]
["RO停机冲洗时间设定-NF系统","ROtjcxsj_sz",null,1]
["RO开机冲洗剩余时间显示-NF系统","ROkjcxsysj_xs",null,0]
["RO运行剩余时间显示-NF系统","ROyxsysj_xs",null,0]
["RO停机冲洗剩余时间显示-NF系统","ROtjcxsjxs_xs",null,0]
["启动-RO系统","ROqd_sz","0:无意义|1:启动",1,"同UF2运行相同"]
["停机-RO系统","ROtj_sz","0:无意义|1:停机",1]
["急停-RO系统","ROjt_sz","0:正常|1:急停",1]
["待机-RO系统","ROdj_sz","0:正常|1:待机",0]
["开机冲洗-RO系统","ROkjcx_sz","0:正常|1:开机冲洗",0]
["运行-RO系统","ROyx_sz","0:正常|1:运行",0]
["停机冲洗-RO系统","ROtjcx_sz","0:正常|1:停机冲洗",0]
["RO高压泵频率给定信号","ROgybpl_sz",null,0]
["UF增压泵2频率给定信号","UFzyb2pl_sz",null,0]
["膜冲洗泵2频率给定信号","mcxb2pl_sz",null,0]
[]
["系统1启动","xt2qd_sz","0:无意义|1:启动",1]
["系统1停止","xt2tz_sz","0:无意义|1:停止"]
[]
[null,"故障状态。该状态支持故障预警及远程设置"]
[null,"组件状态，该状态支持故障预警及远程设置"]
[null,"组件状态。该状态仅展示即可"]
[null,"流程状态。只做展示"]
[null,"系统参数。展示及可远程设置"]
[null,"系统级远程控制，支持远程远程设置"]
[null,"二级系统级控制。展示及可远程设置"]
[null,"暂时不做"]
[]
[{"$nulls":6},"序号","参数项","操作字段","单位"]
[{"$nulls":6},1,"UF1运行时间","UF1yxsj_sz","S"]
[{"$nulls":6},2,"UF1上反洗时间","UF1sfxsj_sz","S"]
[{"$nulls":6},3,"UF1下反洗时间","UF1xfssj_sz","S"]
[{"$nulls":6},4,"UF1正洗时间","UF1zxsj_sz","S"]
[{"$nulls":6},5,"NF高压泵频率","NFgybpl_sz","Hz"]
[{"$nulls":6},6,"膜冲洗泵1频率","mcxb1pl_sz","Hz"]
[{"$nulls":6},7,"UF增压泵1频率号","UFzyb1pl_sz","Hz"]
[{"$nulls":6},8,"NF开机冲洗时间","NFkjcxsj_sz","S"]
[{"$nulls":6},9,"NF运行时间","NFyxsj_sz","S"]
[{"$nulls":6},10,"NF停机冲洗时间","NFtjcxsj_sz","S"]
[{"$nulls":6},11,"UF2运行时间","UF2yxsj_sz","S"]
[{"$nulls":6},12,"UF2上反洗时间","UF2sfxsj_sz","S"]
[{"$nulls":6},13,"UF2下反洗时间","UF2xfssj_sz","S"]
[{"$nulls":6},14,"UF2正洗时间","UF2zxsj_sz","S"]
[{"$nulls":6},15,"RO开机冲洗时间","ROkjcxsj_sz","S"]
[{"$nulls":6},16,"RO运行时间设定","ROyxsj_sz","S"]
[{"$nulls":6},17,"RO停机冲洗时间","ROtjcxsj_sz","S"]
[{"$nulls":6},18,"RO高压泵频率给定信号","ROgybpl_sz","Hz"]
[{"$nulls":6},19,"UF增压泵2频率给定信号","UFzyb2pl_sz","Hz"]
[{"$nulls":6},20,"膜冲洗泵2频率给定信号","mcxb2pl_sz","Hz"]

{"sheet":"方案相关表格","index":3,"n_rows":143,"n_cols":5,"rows_kept":143,"cut":false,"hidden":false,"merged":[[114,0,131,0],[114,1,131,1],[132,0,138,0],[132,1,134,1],[135,1,138,1],[139,0,142,0],[139,1,142,1],[3,0,3,2],[63,0,63,2],[100,0,113,0],[100,1,105,1],[106,1,113,1]]}
[]
[]
[]
[]
["监测项","展示","字段","说明","说明"]
["获取设备数据时间","yyyy-mm-dd hh:mm:ss  "]
["链接状态","在线/离线",null,null,"通信超时判断"]
["运行状态","自动运行/停止运行","zdmskg_sz=1:自动运行|0:停止运行"]
["原料池液位","过高/过低/正常/故障","ylcgyw_zt=1&ylcdyw_zt=0:过高；ylcgyw_zt=0&ylcdyw_zt=1:过低；ylcgyw_zt=0&ylcdyw_zt=0:正常；ylcgyw_zt=1&ylcdyw_zt=1:故障；"]
["污水池液位","过高/过低/正常/故障","wscgyw_zt=1&wscdyw_zt=0:过高；wscgyw_zt=0&wscdyw_zt=1:过低；wscgyw_zt=0&wscdyw_zt=0:正常；wscgyw_zt=1&wscdyw_zt=1:故障；"]
["滤液池液位","过高/过低/正常/故障","lycgyw_zt=1&lycdyw_zt=0:过高；lycgyw_zt=0&lycdyw_zt=1:过低；lycgyw_zt=0&lycdyw_zt=0:正常；lycgyw_zt=1&lycdyw_zt=1:故障；"]
["原料泵输出","打开/关闭/故障","ylbgz_zt=0,ylbsc_sz=0:关闭；ylbgz_zt=0,ylbsc_sz=1:打开；ylbgz_zt=1,ylbsc_sz=x:故障；"]
["挤出机输出","打开/关闭/故障","jcbgz_zt=0,jcbsc_sz=0:关闭；jcbgz_zt=0,jcbsc_sz=1:打开；jcbgz_zt=1,jcbsc_sz=x:故障；"]
["振动点击输出","打开/关闭/故障","zddjgz_zt=0,zddjsc_sz=0:关闭；zddjgz_zt=0,zddjsc_sz=1:打开；zddjgz_zt=1,zddjsc_sz=x:故障；"]
["振荡筛输出","打开/关闭/故障","zdsgz_zt=0,zdssc_sz=0:关闭；zdsgz_zt=0,zdssc_sz=1:打开；zdsgz_zt=1,zdssc_sz=x:故障；"]
["上料泵输出","打开/关闭/故障","slbgz_zt=0,slbsc_sz=0:关闭；slbgz_zt=0,slbsc_sz=1:打开；slbgz_zt=1,slbsc_sz=x:故障；"]
["排污泵输出","打开/关闭/故障","pwbgz_zt=0,pwbsc_sz=0:关闭；pwbgz_zt=0,pwbsc_sz=1:打开；pwbgz_zt=1,pwbsc_sz=x:故障；"]
["滤液泵输出","打开/关闭/故障","lybgz_zt=0,lybsc_sz=0:关闭；lybgz_zt=0,lybsc_sz=1:打开；lybgz_zt=1,lybsc_sz=x:故障；"]
[]
[]
["监测项","展示","字段","说明"]
["获取数据时间","yyyy-mm-dd hh:mm:ss  "]
["链接状态","在线/离线","平台根据链接自行判定"]
["运行状态","自动运行/停止运行","xt1qd_sz=1&xt2qd_sz=1:自动运行；xt1tz_sz=1&xt2tz_sz=1：停止运行","系统级"]
["UF1系统","运行/上反洗/下反洗/正洗/反洗/待机","UF1yx_sz=1：运行；UF1sfx_sz=1：上反洗；UF1xfx_sz=1：下反洗；UF1zx_sz=1:正洗；UF1fx_sz=1：反洗；UF1dj_sz=1:待机","组件级"]
["NF系统","运行/开机冲洗/停机冲洗/待机","NFyx_sz=1：运行；NFkjcx_sz=1：开机冲洗；NFtjcx_sz=1：停机冲洗；NFdj_sz=1:待机"]
["UF2系统","运行/上反洗/下反洗/正洗/反洗/待机","UF2yx_sz=1：运行；UF2sfx_sz=1：上反洗；UF2xfx_sz=1：下反洗；UF2zx_sz=1:正洗；UF2fx_sz=1：反洗；UF2dj_sz=1:待机"]
["UF2系统","运行/开机冲洗/停机冲洗/待机","ROyx_sz=1：运行；ROkjcx_sz=1：开机冲洗；ROtjcx_sz=1：停机冲洗；ROdj_sz=1:待机"]
[]
[]
[]
[]
[]
["监测项","展示","字段"]
["过滤水箱液位","过高/过低/正常/故障","glsxgyw_zt=1&glsxdyw_zt=0:过高；glsxgyw_zt=0&glsxdyw_zt=1:过低；glsxgyw_zt=0&glsxdyw_zt=0:正常；glsxgyw_zt=1&glsxdyw_zt=1:故障；"]
["中间水箱液位","过高/过低/正常/故障","zjsxgyw_zt=1&zjsxdyw_zt=0:过高；zjsxgyw_zt=0&zjsxdyw_zt=1:过低；zjsxgyw_zt=0&zjsxdyw_zt=0:正常；zjsxgyw_zt=1&zjsxdyw_zt=1:故障；"]
["进水阀1","打开/关闭/故障","jsf1kfk_zt=1&jsf1gfk_zt=0:打开；jsf1kfk_zt=0&jsf1gfk_zt=1:关闭；jsf1kfk_zt=jsf1gfk_zt:故障；"]
["冲洗阀1","打开/关闭/故障","cxf1kfk_zt=1&cxf1gfk_zt=0:打开；cxf1kfk_zt=0&cxf1gfk_zt=1:关闭；cxf1kfk_zt=cxf1gfk_zt:故障；"]
["循环阀1","打开/关闭/故障","xhf1kfk_zt=1&xhf1gfk_zt=0:打开；xhf1kfk_zt=0&xhf1gfk_zt=1:关闭；xhf1kfk_zt=xhf1gfk_zt:故障；"]
["上排阀1","打开/关闭/故障","spf1kfk_zt=1&spf1gfk_zt=0:打开；spf1kfk_zt=0&spf1gfk_zt=1:关闭；spf1kfk_zt=spf1gfk_zt:故障；"]
["下排阀1","打开/关闭/故障","xpf1kfk_zt=1&xpf1gfk_zt=0:打开；xpf1kfk_zt=0&xpf1gfk_zt=1:关闭；xpf1kfk_zt=xpf1gfk_zt:故障；"]
["反洗阀1","打开/关闭/故障","fxf1kfk_zt=1&fxf1gfk_zt=0:打开；fxf1kfk_zt=0&fxf1gfk_zt=1:关闭；fxf1kfk_zt=fxf1gfk_zt:故障；"]
["产水阀1","打开/关闭/故障","csf1kfk_zt=1&csf1gfk_zt=0:打开；csf1kfk_zt=0&csf1gfk_zt=1:关闭；csf1kfk_zt=csf1gfk_zt:故障；"]
["产排阀1","打开/关闭/故障","cpf1kfk_zt=1&cpf1gfk_zt=0:打开；cpf1kfk_zt=0&cpf1gfk_zt=1:关闭；cpf1kfk_zt=cpf1gfk_zt:故障；"]
["NF冲洗阀","打开/关闭/故障","NFcxfkfk_zt=1&NFcxfgfk_zt=0:打开；NFcxfkfk_zt=0&NFcxfgfk_zt=1:关闭；NFcxfkfk_zt=NFcxfgfk_zt:故障；"]
["NF进水压力","正常/过低","NFjsyl_zt=1：过低|0：正常"]
["NF产水压力","正常/过高","NFcsgy_zt=1：过高|0：正常"]
["NF高压泵","运行/停止/故障","NFgybyx_zt=1&NFgybgz_zt=0：运行；NFgybyx_zt=0&NFgybgz_zt=0：停止；NFgybyx_zt=x&NFgybgz_zt=1：故障；"]
["膜冲洗泵1","运行/停止/故障","mcxb1yx_zt=1&mcxb1gz_zt=0：运行；mcxb1yx_zt=0&mcxb1gz_zt=0：停止；mcxb1yx_zt=x&mcxb1gz_zt=1：故障；"]
["增压泵1","运行/停止/故障","zyb1yx_zt=1&zyb1gz_zt=0：运行；zyb1yx_zt=0&zyb1gz_zt=0：停止；zyb1yx_zt=x&zyb1gz_zt=1：故障；"]
["阻垢剂加药计量泵1","运行/停止","zgjjlb1yx_zt=1：运行|0：停止"]
["PH加药计量泵","运行/停止","PHjlbyx_zt=1：运行|0：停止"]
["抑菌剂加药计量泵","运行/停止","yjjjlbyx_zt=1：运行|0：停止"]
["UF1运行剩余时间","单位s","UF1yx_sz=1&UF1yxsysj_xs=？"]
["UF1上反洗剩余时间","单位s","UF1sfx_sz=1&UF1yxsysj_xs=？"]
["UF1下反洗剩余时间","单位s","UF1xfx_sz=1&UF1xfssysj_xs=?"]
["UF1正洗剩余时间","单位s","UF1zx_sz=1&UF1zxsysj_xs"]
["NF开机冲洗剩余时间","单位s","NFkjcx_sz=1&NFkjcxsysj_xs=？"]
["NF运行剩余时间","单位M","NFyx_sz=1&NFyxsysj_xs=？"]
["NF停机冲洗剩余时间","单位s","NFtjcx_sz=1&NFtjcxsjxs_xs=？"]
["NF高压泵频率给定信号","单位HZ","NFgybpl_sz=？"]
["膜冲洗泵1频率给定信号","单位HZ","mcxb1pl_sz=？"]
["UF增压泵1频率给定信号","单位HZ","UFzyb1pl_sz=？"]
[]
["中间水箱2液位","过高/过低/正常/故障","zjsx2gyw_zt=1&zjsx2dyw_zt=0:过高；zjsx2gyw_zt=0&zjsx2dyw_zt=1:过低；zjsx2gyw_zt=0&zjsx2dyw_zt=0:正常；zjsx2gyw_zt=1&zjsx2dyw_zt=1:故障；"]
["冲洗水箱液位","过高/过低/正常/故障","cxsxgyw_zt=1&cxsxdyw_zt=0:过高；cxsxgyw_zt=0&cxsxdyw_zt=1:过低；cxsxgyw_zt=0&cxsxdyw_zt=0:正常；cxsxgyw_zt=1&cxsxdyw_zt=1:故障；"]
["进水阀2","打开/关闭/故障","jsf2kfk_zt=1&jsf2kfk_zt=0:打开；jsf2kfk_zt=0&jsf2kfk_zt=1:关闭；jsf2kfk_zt=jsf2kfk_zt:故障；"]
["冲洗阀2","打开/关闭/故障","cxf2kfk_zt=1&cxf2gfk_zt=0:打开；cxf2kfk_zt=0&cxf2gfk_zt=1:关闭；cxf2kfk_zt=cxf2gfk_zt:故障；"]
["循环阀2","打开/关闭/故障","xhf2kfk_zt=1&xhf2gfk_zt=0:打开；xhf2kfk_zt=0&xhf2gfk_zt=1:关闭；xhf2kfk_zt=xhf2gfk_zt:故障；"]
["上排阀2","打开/关闭/故障","spf2kfk_zt=1&spf2gfk_zt=0:打开；spf2kfk_zt=0&spf2gfk_zt=1:关闭；spf2kfk_zt=spf2gfk_zt:故障；"]
["下排阀2","打开/关闭/故障","xpf2kfk_zt=1&xpf2gfk_zt=0:打开；xpf2kfk_zt=0&xpf2gfk_zt=1:关闭；xpf2kfk_zt=xpf2gfk_zt:故障；"]
["反洗阀2","打开/关闭/故障","fxf2kfk_zt=1&fxf2gfk_zt=0:打开；fxf2kfk_zt=0&fxf2gfk_zt=1:关闭；fxf2kfk_zt=fxf2gfk_zt:故障；"]
["产水阀2","打开/关闭/故障","csf2kfk_zt=1&csf2gfk_zt=0:打开；csf2kfk_zt=0&csf2gfk_zt=1:关闭；csf2kfk_zt=csf2gfk_zt:故障；"]
["产排阀2","打开/关闭/故障","cpf2kfk_zt=1&cpf2gfk_zt=0:打开；cpf2kfk_zt=0&cpf2gfk_zt=1:关闭；cpf2kfk_zt=cpf2gfk_zt:故障；"]
["RO冲洗阀","运行/停止/故障","ROcxfkfk_zt=1&ROcxfkfk_zt=0:打开；NROcxfkfk_zt=0&ROcxfkfk_zt=1:关闭；ROcxfkfk_zt=ROcxfkfk_zt:故障；"]
["RO进水压力","正常/过低","ROjsyl_zt=1:过低|0：正常"]
["RO产水压力","正常/过高","ROcsgy_zt=1:过高|0：正常"]
["RO高压泵","运行/停止/故障","ROgybyx_zt=1&ROgybyx_zt=0：运行；ROgybyx_zt=0&ROgybyx_zt=0：停止；ROgybyx_zt=x&ROgybyx_zt=1：故障；"]
["UF2增压泵","运行/停止/故障","UFzyb2yx_zt=1&UFzyb2yx_zt=0：运行；UFzyb2yx_zt=0&UFzyb2yx_zt=0：停止；UFzyb2yx_zt=x&UFzyb2yx_zt=1：故障；"]
["膜冲洗泵2","运行/停止/故障","mcxb2yx_zt=1&mcxb2yx_zt=0：运行；mcxb2yx_zt=0&mcxb2yx_zt=0：停止；mcxb2yx_zt=x&mcxb2yx_zt=1：故障；"]
["NF增压泵","运行/停止/故障","NFzybyx_zt=1&NFzybyx_zt=0：运行；NFzybyx_zt=0&NFzybyx_zt=0：停止；NFzybyx_zt=x&NFzybyx_zt=1：故障；"]
["RO增压泵","运行/停止/故障","ROzybyx_zt=1&ROzybyx_zt=0：运行；ROzybyx_zt=0&ROzybyx_zt=0：停止；ROzybyx_zt=x&ROzybyx_zt=1：故障；"]
["生物减灭器","运行/停止","swjmqyx_zt=1：运行|0：停止"]
["阻垢剂加药计量泵2","运行/停止","zgjjlb2yx_zt=1：运行|0：停止"]
["UF2运行剩余时间","单位s","UF2yx_sz=1&UF2yxsysj_xs=？"]
["UF2上反洗剩余时间","单位s","UF2sfx_sz=1&UF2yxsysj_xs=？"]
["UF2下反洗剩余时间","单位s","UF2xfx_sz=1&UF2xfssysj_xs=?"]
["UF2正洗剩余时间","单位s","UF2zx_sz=1&UF2zxsysj_xs"]
["RO开机冲洗剩余时间","单位s","ROkjcx_sz=1&ROkjcxsysj_xs=？"]
["RO运行剩余时间","单位M","ROyx_sz=1&ROyxsysj_xs=？"]
["RO停机冲洗剩余时间","单位s","ROtjcx_sz=1&ROtjcxsjxs_xs=？"]
["RO高压泵频率给定信号","单位HZ","ROgybpl_sz=？"]
["UF增压泵2频率给定信号","单位HZ","UFzyb2pl_sz=？"]
["膜冲洗泵2频率给定信号","单位HZ","mcxb2pl_sz=？"]
[]
[]
[]
[]
[]
["故障类型","所属单元","故障报警项"]
["设备过载","固液分离单元","原料泵过载"]
[null,null,"挤出机过载"]
[null,null,"振动电机过载"]
[null,null,"振荡筛过载"]
[null,null,"上料泵过载"]
[null,null,"排污泵过载"]
[null,"沼液浓缩单元","NF高压泵故障"]
[null,null,"膜冲洗泵1故障"]
[null,null,"增压泵1故障"]
[null,null,"RO增压泵故障"]
[null,null,"UF增压泵2故障"]
[null,null,"膜冲洗泵故障"]
[null,null,"NF增压泵故障"]
[null,null,"RO增压泵故障"]
["阀门故障","沼液浓缩单元","UF1进水阀"]
[null,null,"UF1冲洗阀"]
[null,null,"UF1循环阀"]
[null,null,"UF1上排阀"]
[null,null,"UF1下排阀"]
[null,null,"UF1反洗阀"]
[null,null,"UF1产水阀"]
[null,null,"UF1产排放阀"]
[null,null,"NF冲洗阀"]
[null,null,"UF2进水阀"]
[null,null,"UF2冲洗阀"]
[null,null,"UF2循环阀"]
[null,null,"UF2上排阀"]
[null,null,"UF2下排阀"]
[null,null,"UF2反洗阀"]
[null,null,"UF2产水阀"]
[null,null,"UF2产排阀"]
[null,null,"RO冲洗阀"]
["液位高低","固液分离单元","原料池高液位过高/过低"]
[null,null,"污水池高液位过高/过低"]
[null,null,"滤液池高液位过高/过低"]
[null,"沼液浓缩单元","过滤水箱高液位过高/过低"]
[null,null,"中间水箱1高液位过高/过低"]
[null,null,"中间水箱2高液位过高/过低"]
[null,null,"冲洗水箱高液位过高/过低"]
["压力高低","沼液浓缩单元","NF高压泵后压力过高"]
[null,null,"RO高压泵后压力过高"]
[null,null,"NF高压泵前压力过低"]
[null,null,"RO高压泵前压力过低"]